## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 05/Sep/2022 | Rev.:06
|  | Comment Sheet Ref.No.: | Doc Description: Instrument Datasheets for Emergency Instrument air compressor
|  | Transmittal No.: APCES-V-00179 | Doc. No.: BU-20-VD-303-IN-DSH-0090
|  | Transmittal Date: 05/Sep/2022 | Doc Rev.: 06
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply | Vendor Clarification (2) | CES Reply (2) | Vendor Clarification (3) | CES Reply (3) | Vendor Clarification (4) | CES Reply (4)
1 | P&ID number to be modified as per related P&ID document number for all instruments. |  |  | Updated in next revision |  |  | Closed.
2 | General comment for all PG/PDG gauges shall be provided with zero stop pin and zero adjustable mechanis, shall be provided. |  |  | Updated in next revision |  |  | Closed.
3 | Ambient / 45°C |  |  | Updated in next revision |  |  | Closed.
4 | As per project specification PDG connection shall be 1/2" NPT |  |  | For PDG 1/4" is standard connection, 1/2" not available. Airpack will supply 1/4"/ 1/2" connectors. |  |  | Closed.
5 | Instrument Air |  |  | Updated in next revision |  |  | Closed.
6 | 0-40 standard range to be considered |  |  | Updated in next revision |  |  | Closed.
7 | Bar (g) |  |  | All other pressures in process and scales are indicated with bar(a) |  |  | Closed.
8 | Gauges with maximum scale value of 25 bar g and more shall be solid front |  |  | Updated in next revision |  |  | Closed.
9 | Please be informed that pipe to be expanded to 4" for installation of TW on pipe |  |  | Noted, however line number as per P&ID. |  |  | Closed.
10 | Stem orientation shall be every angle. |  |  | This is for fieldmounted gauges, not fpr panel mounted. |  |  | Closed.
11 | 10004/ 10002; based on based on vendor PID |  |  | Not clear what you mean please clarify. |  |  | There is no such a comment | Noted
12 | U-length shall be specified by Airpack so that with considering TW tip stai on the middle third of pipe. |  |  | Updated in next revision |  |  | Please specify TW nozzle projection. it seems that selected U-length is too short to TW tip stay on the middle third of pipe. | It is double checked and we confim TW-tip stay on th middel third of pipe. | Closed. It is in vendor responsibility to supply suficant TW length based on project requirements.
13 | Airpack shall submit wake frequency calculations sheets to meet ASME PTC 19.3 to purchaser for approval. |  |  | This has not been agreed upon in the contract. |  |  | Please attach related MOM or TCL about this agreement. | Please mention where this is mentioned in the specification | According to signed MRQ by Airpack, section RFD, page 26, clause TE97 "Stress analysis and Calculation for thermowell" shall be supplied by Airpack.(your temp. element sub-vendor must submit wake frequency calculation)
14 | XY-10002 is one of the XV-10002 accessories it shall be removed and mentioned in On-off valve datasheet. |  |  | As it has a separate Tag number a seperated dataheet has been incorporated and not only an accessorie of valves. |  |  | Solenoid valve shall has a separate tag no. but it is one of the XV-71102 accessories and must be mentioned in on-off valve data sheet and removed from this data sheet. | Cross reference will be made on the XV-10002 datasheet referinge to the XY-10002 datasheet | Closed.
15 | - Please issue this document after P&ID approval and received sub-vendor complete information. |  |  | P&ID has been updated, inquiries for instruments are sent after approval of drawings, only af that the fnal information will be submitted. So please first approve the items as they are now so we can sent inquiries to our sub-vendors. |  |  | Noted, instrument MFR and model must be specified after data sheet approval. | noted | Comment was not implemented.
16 | - Manufacturer and Model no. for all items must be specified. |  |  | see reply Item 11 |  |  | See reply Item 11 |  | Comment was not implemented.
17 | - All "VTA" and "To be advised by supplier" and etc. to be specified in next rev. |  |  | see reply Item 11 |  |  | See reply Item 11 |  | Comment was not implemented.
19 | 85 oC.the comment is valid for other instruments on the line. |  |  | Updated in next revision |  |  | Closed.
21 | 100 oC.Must be consider for all cooling water lines |  |  | 95°C as per PID will be updated in next revision. |  |  | Not accepted. The comment must be taken unto consideration. | D.T is 95°C as per P&ID | PR Reply: Closed
22 | 7 barg. Must be consider for all cooling water lines. |  |  | 10 barg as per PID will be updated in next revision. |  |  | Not accepted. The comment must be taken unto consideration. | D.P is 10 barg as per P&ID | PR Reply: Closed
23
23 | Current revision is REV.02 |  |  | Updated in next revision |  |  |  |  | Closed.
24 | in PTD OT (shell is reported 180°C |  |  | Updated in next revision |  |  |  |  | Closed.
24 | Based on Basis of design of the project design temperature must be specified by the following rule: |  |  | D.T updated are as per P&ID. |  |  |  |  | Closed.
| Design temperature for PROCESS equipment shall whichever is higher: | [7 empty] | Closed.
| • maximum operating temperature +15°C (+25°C for Feed/Effluent exchanger) | [7 empty] | Closed.
| • boiling temperature at design pressure of PROCESS medium inside, if applicable | [7 empty] | Closed.
| Design temperature shall be rounded up to full 5°C steps | [7 empty] | Closed.
| Design minimum temperature shall be specified only if the minimum operating temperature is below 0°C. Design minimum temperature shall be 5°C less than the minimum operating temperature. Special attention shall be given to low boiling liquids such as LPG. | [7 empty] | Closed.
| For piping, design temperature shall be determined according to ASME B31.3. | [7 empty] | Closed.
| The comment is valid for all instruments . | [7 empty] | Closed.
25 | Based on Basis of design of the project design pressure must be specified by the following rule: |  |  | D.P are as per P&ID. |  |  |  |  | Closed.
| Design pressure of process static EQUIPMENT shall be based on the max. operating pressure. | [7 empty] | Closed.
| Malfunction and EQUIPMENT failure shall be taken into consideration by safety devices. | [7 empty] | Closed.
| Design pressure shall be selected from the list below: | [7 empty] | Closed.
| • for max operating pressure below 2 barg use 3.5 barg | [7 empty] | Closed.
| • for max operating pressure between 2 barg and 15 barg use max operating pressure +1.5 bar | [7 empty] | Closed.
| • for max operating pressure between 15 barg and 100 barg use max operating pressure x 110% | [7 empty] | Closed.
| • for max operating pressure equal and above 100 barg use max operating pressure +10 bar | [7 empty] | Closed.
| The comment is valid for all instruments. | [7 empty] | Closed.
26 | Gauge savers shall be considered for the services such that full scale of the gauge is smaller than its design pressure. |  |  | Full scale range will be updated in next revision. |  |  |  |  | Closed.
27 | Repeated comment; Airpack shall submit Wake Frequency calculation sheets to meet ASME PTC 19.3 to purchaser for approval. |  |  | Calculations are not part of the agreed scope of supply. |  |  |  |  | According to signed MRQ by Airpack, section RFD, page 26, clause TE97 "Stress analysis and Calculation for thermowell" shall be supplied by Airpack.(your temp. element sub-vendor must submit wake frequency calculation)
28
28 | Manufacturer and model no. must be specified after data sheet approval or approved as note. also "VTA" , "To be advised by supplier" and etc. must be specified too. |  |  | Updated in next revision "AFC" after purchase. |  |  | Closed. | [5 empty] | CLOSE
29 | Data sheet and calculation sheet for FO-71101 and FO-71102 that recently added in P&ID shall be bring in this document. (please refer to attached file for sample format of FO data sheet) |  |  | first of all no sample format was received, secondly this is calculation from API 618 approach 2, so the information regarding the FO can be found there and will not be added to this datasheet |  |  | Sample FO data sheet shall be filled out by vendor. CES comment is not related to pulsation dampener calculation. | Will be updated in next revision. |  |  |  |  | Some data are missed in orifice plate data sheet, please follow attached file.
30 |  |  |  | Design pressures are as per design pressures on the P&ID, as there were no comments on the P&ID, the same design pressure will be followed. |  |  | The vendor is to follow the project criteria and is the sole responsible. Also, Design pressure cannot be less than PSV set pressure (For example, PSV-71101 set pressure is 26 barg, but PG-71105 design pressure is 26 bara). | Design pressure as per P&ID | The vendor Documents must be consistent. Also, Airpack has considered PSV set pressure as operating pressure which is not correct and shall be deleted from instrument data sheet. Design pressure in no way shall not be less than PSV set pressure considering clause 7.6.5 of API 618 5th edition. | PSV-71101 set point on the P&ID will be changed into 24 bar(a), Max. & Design pressure on the datasheet will be changed into 25 bar(a). | Document shall be revised considering PSV set pressure on latest revision of P&ID. | Will be updated in next revision | CLOSE
31 | Repeated comment; Airpack shall submit Wake Frequency calculation sheets to meet ASME PTC 19.3 to purchaser for approval. |  |  | According to signed MRQ by Airpack, section RFD, page 26, clause TE97 "Stress analysis and Calculation for thermowell" shall be supplied by Airpack.(your temp. element sub-vendor must submit wake frequency calculation), however it is only mentioned if applicable, and it is not menioned in the specifcation if it is applicable. therefore it has not been considered |  |  | Wake frequency calculation is applicable for thermowells, and also as per ESS for Package Instrumentation 1216-DE-00-IN-ESS-603 page 48 of 75 "The design of the thermowells shall be verified for all items by vendor by means of stress analysis, resulting from stream velocity condition. Frequency limitation shall meet ASME PTC 19.3 TW-2010. Vendor shall submit the calculation sheets to purchaser for approval." Similar to other packages in this project, Airpack must submitted wake frequency calculation. | Please refer to MR, we can offer it against extra costs | Wake frequency calculation is a part of your contract as per mentioned in previous reply and you are not specify it as a deviation in your deviation list, so you must submit calculation and also extra cost is not accepted for this issue. Please specify fluid velocity in the data sheet | again it is not a deviation, since it is not specified in your datasheets. In the MR it is mentioned that if it is applicable, however it is not menioned that it is applicable and therevore it is not considere a deviation. We will only do this against extra cost, since it is not calculated in our offer. | As per previous reply, vendor shall specify fluid velocity in data sheet. After that we will check it, if velocity is suitable, calculation is not required. but if it is critical, calculations shall be submitted by vendor. | Velocitys are calculated as follows: TG-71103/04: 0,1 m/s TIT-71101: 0,2 m/s TIT-71102: 0,1 m/s | Noted, With considering that wake frequency calculation has not been submitted by vendor so following dimensions of thermowell shall be specified in TW data sheet : • Root diameter • Tip diameter • Tip thickness • Bore diameter • Nozzle projection
28
32 | Discrepancy with instrument index please clarify. |  |  | instrument index has been updated, to be correct in next revision
33 | Comments in this page are applicable for other Thermowell too. |  |  | Noted and updated
34 | With considering that wake frequency calculation has not been submitted by vendor so following dimensions of thermowell shall be specified in TW data sheet : • Root diameter • Tip diameter • Tip thickness • Bore diameter • Nozzle projection |  |  | Noted and updated
35 | To be specified |  |  | Noted and updated
36 | Manufacture and model no. shall be specified |  |  | Noted and updated
37 | To be specified |  |  | Noted and updated
38 | Orifice data sheet is not complete some data such as follow must be added (also you can use attached FO data sheet to the reply sheet) : • Sizing standard (ISO 5167) • Type of bore (Concentric square edge or etc.) • Orifice bore diameter • Beta ratio • Plate thickness • Plate material |  |  | Noted and updated
39 | Wall thickness is thinner than dimensional Limits listed in ASME PTC 19.3 TW-2010 Tables 4-1-1 or 4-2-1 |  |  | specification only mentiones ASME PTC 19.3 TW-2010 Tables 4-1-1 or 4-2-1 for calculation, since this was not included. This is not followed. Also if you insist, it will be against extra cost, since this comment was given late thermowells haven already been menufactured
40 | Root diameter shall be 25 mm Tip diameter shall be 19 mm Tip thickness shall be 6.4 mm Bore diameter shall be 6.6 mm |  |  | specification only mentiones ASME PTC 19.3 TW-2010 Tables 4-1-1 or 4-2-1 for calculation, since this was not included. This is not followed. Also if you insist, it will be against extra cost, since this comment was given late thermowells haven already been menufactured
41 | due to the nozzle projection and U-length, thermowell will not fitted in its place, accordingly nozzle projection shall be modified so that thermowell properly fitted and also tips of thermowell to be in the middle third of pipe. |  |  | Nozzle projection110 mm will be updated
42 | Comments in this page are applicable for other Thermowell too. |  |  | Noted and updated
43 | Line size to be specified |  |  | Noted and updated
44 | Plate thickness shall be greater than 0.12D |  |  | this is not the case in the orrifice, the calculaton comes from API 618 pulsation study, therefore calculation will not be done in ISO 5167
45 | As per project specification "Orifice bores shall be calculated by using the formula based on ISO 5167." |  |  | this is not the case in the orrifice, the calculaton comes from API 618 pulsation study, therefore calculation will not be done in ISO 5167
46 | Material shall be specified with ASTM code |  |  | ASTM A694 F52 will be updated.
47 | Comments in this page are applicable for other FO. |  |  | Noted and updated