## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 05/Sep/2022 | Rev.:06
|  | Comment Sheet Ref.No.: | Doc Description: INSTRUMENT INDEX FOR NITROGEN COMPRESSOR
|  | Transmittal No.: APCES-V-00179 | Doc. No.: BU-20-VD-303-IN-INX-0032
|  | Transmittal Date: 05/Sep/2022 | Doc Rev.: 06
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CHCE Reply | Vendor Clarification (2) | CHCE Reply
1 | As I/O list did not supplied by vendor so all required items in I/o list to be added to index. -Signal Type (4-20mAmp, 24vdc , ...) -From/ To And also all signals to be indicated in this doc (limit switch of valves , remote start stop command (refer to page 4&6 OF pid) |  |  | Noted. Additional I/O information will be added to the existing instruments, and signals to/from ESD/FCS/DB will be added as per P&ID. |  |  | Noted |  | Closed.
2 | This document is checked only for compressor 7080. New document should be generated for compressor 1002. |  |  | New documents will be one instrument index for compressor 1002, and one for compressor 7080. |  |  | Noted |  | Closed.
3 | As per project spec redundancy to be considered where required (for example closed loops) |  |  | Noted. Redundant I/O will be indicated. |  |  | Redundancy is not specified, please modify. | Redundancy is specified underneath I/O TYPE column. | Closed.
4 | To be corrected |  |  | Noted, it will be updated |  |  | PID, Data sheet, wiring and Hook-up document number shall be modified as per VPIS. | Noted. It will be incorporated. | Closed.
5 | There is a deviation between this doc and PID in sequence of tag numbers, please clarify? |  |  | The tag numbers will be updated according to per P&ID. |  |  | Please refer to comment on nitrogen PID for instrument numbering procedure. | Tag numbers are as per P&ID. | Closed.
6 | To be filled carefully,there is not any signal for local gauges. |  |  | Noted. The signals for local gauges will be removed. |  |  | Noted |  | Closed.
7 | Refer to comments on data sheet |  |  | Noted. It will be udpated according to per data sheet. |  |  | Noted |  | Closed.
8 | isolation valve for LG to be considered |  |  | As per P&ID, there's no isolation valve for LG. |  |  | Noted |  | Closed.
9 | For on/off valve DO signals will be considered for solenoid valve not ball valves |  |  | Noted, it will be updated |  |  | Noted |  | Closed.
10 | following items to be added to index: VT FT |  |  | Noted, it will be incorporated |  |  | Noted |  | Closed.
11 | Same as comment on C-1002 |  |  | Noted |  |  | Noted |  | Closed.
12 | *Reply sheet shall be submitted by vendor *Please refer to comment in PID for instrument numbering procedure *PID, data sheet, wiring and hook-up document number shall be modified as per VPIS *This document will be finalized after PID and data sheet approval and considered all comments *PSV-1001 shall be added to teh instrument list *Manufacturer adn model no. to be specified in this document |  |  | Noted |  |  | - Noted. - Noted, But revised PID shall be issued before this document. - Noted. - Please issue next revision of this document after PID approval, also instrument manufacturer and model no. specified. - Noted. - MFR and model are not specified. | Noted. This document is issued according to per P&ID. MFR and model will be specified after placing the order. | Noted, please revise this document after specify mentioned items from your sub-vendor.
13 | Abbreviation to be specified. Please clarify about "DB" |  |  | Distribution board |  |  | Noted. |  | Closed.
14 | Tags to be modified as per comment on PID |  |  | Noted |  |  | It has not been implemented | Tags as per P&ID. | Closed.
15 | Service desctiption to be modified |  |  | Noted |  |  | Noted. |  | Closed.
16 | I/O redundance to be specified |  |  | Noted |  |  | It has not been implemented | Redundancy is specified underneath I/O TYPE column. | Closed.
17 | - Revised P&ID shall be issued before this document, latest revision of P&ID (rev.1) is not conformity with instrument index. - Manufacturer and model no. shall be specified in next revision. |  |  | Noted. This document is issued according to per P&ID. MFR and model will be specified after placing the order. |  |  | Noted, please revise this document after specify mentioned items from your sub-vendor.
18 | General Notes 1. Any modification must be highlighted. 2. All documents must be consistent with each other in terms of tag numbers, line numbers and so on. 3. It is not clear why tag numbers are being changed, yet this document will be finalized when PID is issued. |  |  | 1. Noted. Modification will be highlighted. 2. Noted. Tag numbers as per P&ID. 3. This document is issued according to per P&ID |  |  | Closed.
19 | This document will be approved after receiving new revision of P&ID |  |  | Noted. This document is issued according to per P&ID |  |  | Closed.
20 | To be specified |  |  | It will be specified after placing the order. |  |  | Noted, please revise this document after specify mentioned items from your sub-vendor.
21 | Tags to be modified as per comment on PID. |  |  | Noted. Tags as per P&ID. |  |  | Closed.
22 | Redundant I/O shall be considered |  |  | Noted. It will be modified. |  |  | Closed.
23 | Tag number to be specified |  |  | Please advise and specify the unspecified tag numbers. |  |  | Please refer to I/O List and revised accordingly
24 | Manufacturer and model no. shall be specified in next revision. |  |  | Updated |  |  | Closed.
25 | All "TBA", "to be advised", "will be stated later" and ect. items shall be specified. |  |  | Updated |  |  | Closed.
26 | Not found in PID |  |  | PG-10161 has been founded in the P&ID CES Reply: Closed. |  |  | Closed.
27 | Tag number has discrepancy with PID |  |  | There is no difference in tag number with the P&ID CES Reply: Closed. |  |  | Closed.
28 | Tag number to be specified. (according to I/O List) |  |  | Noted. It will be modified. |  |  | Closed.
29 | IS/NIS for all signals shall be specified. |  |  | Noted. It will be modified. |  |  | Closed.
30 | 13 |  |  | Updated |  |  | Closed.
28 | 50 |  |  | Updated |  |  | Closed.
29 | 160 |  |  | Updated |  |  | Closed.
30 | Discrepancy with PID. In PID 1/2" |  |  | Noted. It will be modified. CES Reply: Closed. |  |  | Closed.
28 | Discrepancy with PID. In PID it is High alarm. Besides, TAHH-10153 stands for HH alarm. |  |  | Already updated CES Reply: Closed. |  |  | Closed.
29 | considering the fact that both PIT-10157 and PIT-10156 are on the same line, it must be clarified how it is possible that LL alarm is higher than high alarm. |  |  | Updated CES Reply: Closed. |  |  | Closed.
30 | To be deleted |  |  | Moved to SET POINT H |  |  | Closed.
28 | Discrepancy with P&ID in valve size please clarify |  |  | Valve size updated in the Instrument index to 2'' |  |  | P&ID shall be modified accordingly.
29 | Discrepancy with PID. In PID it is 2" |  |  | Updated CES Reply: Closed. |  |  | Closed.
30 | PSV inlet/outlet size shall be specified |  |  | Updated |  |  | Closed.
29 | Please specify : TBC |  |  | Noted, will be updated in next revision |  |  | Closed.
30 | Model no. to be modified as per data sheet |  |  | Noted, will be updated in next revision |  |  | Closed.
31 | Discrepancy with PID. In PID 1 1/2" (according to I/O List) |  |  | Noted, will be updated in next revision
32 | To be specified |  |  | Noted, will be uploaded in the next revision. VT-71151 : The integral cable of the compressor vibration transmitter defines the process connection . The size of this cable is not known until the purchase is made. |  |  | Noted.
33 | 2) Based on PID LL and HH alarm are not considered for PIC-10158 |  |  | Confirmed, according to the P&ID and Instrument datasheet PIDH=23,5 Bar (a) and PIDL=22. Will be updated in next revision Bar(a) |  |  | Closed.
34 | 24 |  |  | Confirmed, will be uploaded in next revision. |  |  | Closed.
35 | 1) 23.5 |  |  | Confirmed, will be uploaded in next revision. |  |  | Closed.
36 | To be deleted |  |  | Noted, will be updated in next revision |  |  | Closed.
37 | Following tag shall be added to the index : • FO-10151 • FO-10152 • FO-10153 • FO-10154 |  |  | Noted, will be added in next revision |  |  | Closed.
38 | Valve and actuator MFR/Model no. to be specified. |  |  | Noted, will be updated in next revision.
39 | Model no. to be modified as per data sheet |  |  | Noted, will be updated in next revision.
40 | Discrepancy with data sheet Please clarify |  |  | Noted, will be updated in next revision.
41 | 1/2" NPT-M |  |  | Noted, will be updated in next revision.
42 | For ROs "System Type" to be filled with dash(-). |  |  | Noted, will be updated in next revision.
43 | Discrepancy with PID. In PID 100 °C |  |  | Noted, will be updated in next revision.
44
45
46
47
48
49
50