## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 30/Jun/2022 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: MODBUS LIST FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00157 | Doc. No.: BU-20-VD-303-IN-LST-0102
|  | Transmittal Date: 30/Jun/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification
1 | Prerequisite document such as I/O list shall be issued. This doc to be updated based on comments on index and also as per project PID (for interface signals between PLC and main system) |  |  | Noted. It will be incorporated. CES REPLY: Please don't issued this document until I/O list and P&ID are not approved.
2 | LOGO CES |  |  | Noted. It will be incorporated. CES REPLY: Closed.
Rev01
3 | Please add modbus configuration parameter same as following; - General data {Protocol, Baudrate} - Primary Master parameters { Master Id, Interface, IP address, Subnet Maskt, Gateway} - Primary Slave Paramters {Slave Id, Interface, IP address, Subnet Mask, Gateway} - Secondary Master parameters { Master Id, Interface, IP address, Subnet Maskt, Gateway} - Secondary Slave Paramters {Slave Id, Interface, IP address, Subnet Mask, Gateway} |  |  | Communication parameters added. Please check and correct if they are incorrect or not possible. CES REPLY (06.13.2022): PLEASE SEE THE COMMENT IN THE DOCUMENT
Rev02
4 | Row 48, tag to be specified [compressor B forced shutdown] |  |  | Noted. It will be incorporated.
5 | Change 'common alarm' to 'Compressor S/D status'. |  |  | Noted. It will be incorporated.
6 | Primary and secondary IP address can't be the same |  |  | Changed Primary slave to '192.168.10.30' and Secondary slave parameters to '192.168.10.40'
7 | Primary Master parameters and Secondary Master parameters need to be specified |  |  | Noted. It will be incorporated.
8 | Interface card model number to be specified |  |  | Noted. It will be incorporated. Model no is: CP343-1