## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 05/Jul./2022 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: System architecture drawing
|  | Transmittal No.: APCES-V-00159 | Doc. No.: BU-20-VD-303-ME-DIG-0044
|  | Transmittal Date: 05/Jul/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification
1 | - Abbreviation and signal type to be specified in the legend. - System BOM shall be specified in "UCP/LCP/JB WIRING DIAGRAM" and BOM for other devices such as laptop, OWS and etc. shall be specified in this document. |  |  | - noted and updated - BOM of EWS and OWS, already in datasheet. Not required to be mentioned here\ CES Reply : Closed
2 | Scope of supply sign for cable to be specified |  |  | noted and updated CES Reply : Closed
3 | to be deleted |  |  | noted and updated CES Reply : Closed
4 | DCS to be modified to FCS |  |  | noted and updated CES Reply : Closed
5 | EWS |  |  | noted and updated (Updated based on discussion of extra costs) CES Reply : Closed
6 | to be deleted |  |  | noted and updated CES Reply : Closed
7 | 110 VAC |  |  | noted and updated CES Reply : Closed
8 | Abbreviations shall be specified in legend |  |  | noted and updated CES Reply : Closed
9 | To be deleted, UPS/ Non-UPS feeders are deliverd to vendors UCP in control room |  |  | noted and updated CES Reply : Closed
10 | This note is not related to engineering document and shall be deleted. |  |  | Note update, 1 laptop for 2 packages.
11 | FCS |  |  | noted and updated
12 | Nitrogen Compressor |  |  | noted and updated