## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 07/Jul/2022 | Rev.:03
|  | Comment Sheet Ref.No.: | Doc Description: Calculation & Datasheet of Safety valves for Emergency instrument air compressor
|  | Transmittal No.: APCES-V-00161 | Doc. No.: BU-20-VD-303-IN-DSH-0068
|  | Transmittal Date: 07/Jul/2022 | Doc Rev.: 03
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | 1. The line does not have number in PID. Besides, please clarify why class of the line is 539D. |  |  | Class is 500C, line nr.N/A will be updated in next revision. CES Reply: Please be noted that the PSV is located on the outlet of the compressor (instrument air), so the class of the line cannot be 500C.
2 | 2. Please clarify why design pressure of PSV is less than its set pressure. |  |  | Updated in next revision CES Reply: Closed.
3 | 3. 52 oC |  |  | Updated in next revision CES Reply: Closed.
4 | Size has discrepancy with PID please modify. |  |  | Updated in next revision P&ID
5 | 4. 500C(N) |  |  | Will not be incorporated is as per P&ID CES Reply: Please be noted that the comment was made based on the vendor PID.
6 | As per project spec. : All safety relief valves, shall have flanged inlet and outlet connections of 300 # RF and 150 # RF respectively |  |  | Will not be incorporated as per seperate discussion by E-mail.
7
8 | 2) 500 C(N) |  |  | noted and updated
9 | 1) 7barg |  |  | 3.5 bar(g) as per P&ID, this is the correct setting eventhough design pressure is 7 bar(g).
10
11
12
13
14
15
16
17
18
19
20
21