## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 14/Jul/2022 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: ELECTRICAL LOAD LIST FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00162 | Doc. No.: BU-20-VD-303-EL-LST-0096
|  | Transmittal Date: 14/Jul/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification
1 | According to DSH, IP56 is true. Please clarify which is correct? It has conflict with C-1002. |  |  | noted and updated
2 | According to DSH: 11.5kW Please clarify which is correct? |  |  | noted and updated
3 | According to DSH: Locked Rotor Power Factor = 0.5 Please clarify which is correct? |  |  | noted and updated
4 | According to DSH: Ex d IIB T4 |  |  | noted and updated
5 | According to DSH: 4x6 mm2 M25 Please clarify which is correct? (Cable from panel to motor is in vendor's scope of work.) |  |  | noted and updated
6 | 400VAC is equal to 3ph. |  |  | noted and updated
7 | This is a distribution board and is not a motor. Duty operation shall be clarified |  |  | noted and updated
8 | C-1002 or C-7080? Please check it. |  |  | noted and updated
9 | As per VPIS there is not any document related to panel heat dissipation. Please clarify. |  |  | Noted, has been deleted
10
11
12