## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 14/Jul/2022 | Rev.:03
|  | Comment Sheet Ref.No.: | Doc Description: UCP/LCP/JB WIRING DIAGRAM FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00163 | Doc. No.: BU-20-VD-303-IN-DIG-0093
|  | Transmittal Date: 14/Jul/2022 | Doc Rev.: 03
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply (Nov.04,2021) | CES Reply (June.06,2022)
1 | - Reply sheet shall be submitted by vendor. - Reference document to be specified. - Prerequisite document such as architecture diagram and I/O list shall be issued before this document. - After FAT minimum of 20 % installed spare in all respects shall be available. - UCP, LCP and JB tag to be modify as per comments on page 2 of P&ID. - Component list BOM same as below table shall be add |  |  | - Noted - Noted - Noted - Noted - Noted - Updated in next revision |  |  | - Closed. - Reference documents are not specified. Updated - Architecture is not issued this shall be send after the wiring diagram - This item will be review after I/O list finalized. noted - Closed. - BOM was not added in the panel laypout all the parts are added and in the wiring diagram the device tag list is added with all components
2 | MARK EXd Please confirm that following specification as per project standard is applicable for cable glands. |  |  | Updated in next revision Exd only for distribution panel Confirmed |  |  | - Closed - With reference to TCL, JBs shall EXD. Airpack comment: BU-20-D-000-IN-DSH-627-03 JUNCTION BOXES AND CABLE GLANDS specification followed no exd jb shall be used only for terminald jb's - Noted for cable gland. | TQ SHALL BE SUBMITTED
3 | UCP-C7080-01 |  |  | Updated in next revision |  |  | Closed.
4 | EL.03: Use circuit breakers to protect the circuit. if a fault occurs after switches, it might upstream C.B to trip and it's not logical. EL02: Incoming power supply terminal numbers shall be clarified. EL.04: Add a page and show the legend and symbol list. Ventilation system shall be use UPS power supply. |  |  | Circuit breakers are used after the switches for the panel to trip Clarified with text left from terminal block Updated in next revision Ventilation system shall be from NON-UPS as per wiring diagram |  |  | EL03: not accepted. circuit breaker shall be considered in incoming. EL02: Noted. EL04: not accepted. it in not complete and shall be checked and revised. This is included in the wiring diagram it's called the device tag list Ventilation comment is not related to ELEC and shall be replied by INST. | Noted
5 | Solenoid valves shall be I.S. with 24 VDC voltage rating. |  |  | Solenoids are NON-IS as per project specification |  |  | Closed.
6 | Modbus TCP/IP shall be considered |  |  | Updated in next revision |  |  | Closed.
7 | 20 % spare to be consider |  |  | Updated in next revision |  |  | This item will be review after I/O list finalized. noted
8 | Solenoid valves shall be I.S. with 24 VDC voltage rating. JIDX-C7080-xx xx=your sequence General comments for JB wiring - Cable type, color and gland size shall be specified and followed same as attached file. - JB and LCP layout shall be added same as attached file. - Entry for multi-pair cables to junction box shall be from bottom. - The minimum degree of protection shall be IP 65. - Terminals shall be certified EEx 'e' (for EEXi and Non EExi signals) in accordance with IEC/CENELEC standards IEC 60079. - The following color codes shall be considered for body of each Junction box: • EEx "e" JB, shall be green (RAL 6021). • EEx "d" JB, shall be gray (RAL 9006). • Each junction box in Intrinsically Safe circuit shall be blue (RAL 5015). - Each box shall have terminal blocks with the following characteristics: • Terminal blocks shall be spring loaded Klippon type and vibration proof • Rating of terminal blocks shall be 600V as minimum • Number of terminals in each junction box shall be 16 or 31 or 41 or 61 - Screens shall be insulated from earth at instrument side. They shall be continuous through to the control room marshaling cabinet where they will be connected to the clean system. |  |  | Solenoids are NON-IS as per project specification, rating is 24VDC Updated in next revision - Updated in next revision - Noted - Confirmed - Confirmed - • Noted • Noted • Noted - • Noted • Noted • Noted - Updated in next revision |  |  | - Closed. - For JB and LCP layout comment please refer to BU-20-VD-303-IN-DWG-0039-01 BU-20-D-000-IN-DSH-627-03 followed - Eex'e' certificate for terminals shall be mentioned as a note and specified in BOM. Noted
9 | Individual and overall screen terminals shall be considered. as per general comment 16 terminal to be consider. |  |  | Updated in next revision |  |  | Closed.
10 | Terminal for overall screen to be consider |  |  | Updated in next revision |  |  | Closed.
11 | - One multi cable is consider for analogue input/output signals, please merge this terminal strip with analogue inputs terminal strip in previous page |  |  | Noted |  |  | Closed.
12 | EL.05: Use circuit breakers to protect the circuit. if a fault occurs after switches, it might upstream C.B to trip and it's not logical. |  |  | Circuit breakers are used after the switch for the panel to trip |  |  | not accepted. ciruit breaker shall be considered for incoming. Circuit breakers for incoming power you need to provide before it's coming inside the panel, inside the panel and for all conponents airpack have included mcb's so after the main switches and before the power converters this is per project specification | Noted
13 | EL.06: Add following data in the box. From: SWB3A-03(0.4KV) Cable no: EBP-20-C-7080-M Cable Type and Size: CU/XLPE/AWA/PVC3.5*50mm2 Gland: EX-IP66, C2/M40 |  |  | Noted, Updated in next revision |  |  | it is not completed. Refer to coment on document. ( also please note that cable shall be cu/xlpe/swa/pvc, not awa) Updated | Noted
14 | EL.07:It's recommended to change the place of Bi-metal and Contactor with each other, EL.08: It shall be 6In EL.09: Specify the CT and Ammeter's data completely. EL.10: Why this contact is used in negative side? Is it standard to connect 24vdc directly to the coil then switch it from negative side? EL.11: Use 3K12 to indicate Running and Stopped position of the motor. (use 2 signal lamps) |  |  | This is the way it should be Updated in next revision This shall be added in the spare part list, this is another document Updated in next revision This are already 2 lamps, 1 for permissive and 1 for fault Updated as per latest P&ID |  |  | EL07: closed. EL08: closed. EL09: not accepted. details shall be added in this drawing beside CT and ammeter symbols. CT added EL10: closed. EL11: emphasized again. This is per P&ID so comment on the P&ID | EL07 ~ EL10 : Noted EL11: Not Acceptable.
15 | EL.12: Specify the type and rating of C.B. EL.15: It seems using this aux. relay as Heater Running in this part of the circuit is not sounds suitable, because after that there is a SSR switch and it might be in open status. Please check and clarify. EL.13: Please clarify about the thyristor switch. Add all switch data beside of it, EL.16: Does SSR have any error contact to using in circuit? EL.14: Add all aux. relay's name beside them. EL.17: Is it standard to connect 24vdc directly to the coil then switch it from negative side? Please clarify it. EL.18: Panel layout arrangement shall be prepared and issued. EL.19: Part list shall be added in document. EL.20: Other parts of the wiring document shall be checked by Instrument dep. |  |  | Noted Wiring changed since thermostat is added Wiring changed since thermostat is added Yes inside the UCP panel Yes this is correct Noted Updated in next revision Noted |  |  | EL12: emphasized again. Type shall be added in the spare part list. EL15: it shall be clarified. This is suitable and checked EL13: it shall be clarified. Type shall be added in the spare part list. EL:16: closed. EL14: emphasized again. Updated check all aux references in the wiring diagram for description EL17: closed. EL18,19,20: emphasized again. Part list is added with all information | Noted
16 | - Please refer to comments on I/O List, P&ID and other relevant document. - After FAT minimum of 20 % installed spare in all respects shall be available. - Ventilation system (110 V, 50 Hz, UPS) fitted with dust filters and with extraction fans mounted on the top of cabinets shall be provided. - Multi cable for connection pushbuttons and lamps on LCS not specified, please consider one 10Pair cable for LCS signals to UCP and arrange terminal strip accordingly. - PB-71103 on local panel, for compressor ESD PB, I/O card connection is missed. - XS-715 signal and wiring diagram is missed. - Related I/O card for emergency shut down command from ESD to be specified and also ESD command on the UCP panel. - Please modify device tag list in page 8 same as following table : I24 |  |  | - Noted - Noted - fan with filter is included - updated - XS-715 add also to input plc - Updated - noted |  |  | - Closed -Closed -Closed -Closed -Closed -Closed
17 | (RAL 9006) Gray Eex'd' as per TCL shall be selected. IE connection shall be separate to two bar one as ISE for IS signals and the other one as NISE for NIS signals. |  |  | BU-20-D-000-IN-DSH-627-03 JUNCTION BOXES AND CABLE GLANDS specification followed no exd jb shall be used only for terminald jb's BU-20-D-000-IN-DSH-627-03 JUNCTION BOXES AND CABLE GLANDS specification followed no exd jb shall be used only for terminald jb's Exe jb shall be used. ISE shall be added and PE. |  |  | Closed.
18 | EL-03: description shall be specified. |  |  | Updated and done (closed) |  |  | Closed.
19 | FCS |  |  | Updated and done (closed) |  |  | Closed.
20 | EL.01: Use circuit breakers to protect the circuit. if a fault occurs after switches, it might upstream C.B to trip and it's not logical. |  |  | Circuit breakers for incoming power you need to provide before it's coming inside the panel, inside the panel and for all conponents airpack have included mcb's so after the main switches and before the power converters this is per project specification |  |  | Closed.
21 | EL02: Incoming power supply terminal numbers shall be clarified. |  |  | Updated (closed) |  |  | Closed.
22 | - Please clarify to considering display page on the panel door. - As per MR vendor must consider industrial workstation too.I37:N38 |  |  | - display is on panel door - not part of the wiring diagram |  |  | Closed.
23 | Tag to be modified |  |  | Updated (closed) |  |  | Closed.
24 | ESD |  |  | Updated (closed) |  |  | Closed.
25 | EL.08: Add following data in the box. From: SWB3A-03(0.4KV) Cable Type and Size: CU/XLPE/AWA/PVC3.5*50mm2 Gland: EX-IP65, C2/M40 |  |  | Updated (Closed) |  |  | Closed.
26 | EL-04: Use circuit breakers to protect the circuit. if a fault occurs after switches, it might upstream C.B to trip and it's not logical. |  |  | This is with MCB protection |  |  | Closed.
27 | EL-05: Single line diagram document shall be revised based on this document. |  |  | Noted |  |  | Closed.
28 | EL-07: complete legend sheet shall be added for power distribution panel items. |  |  | Noted |  |  | Closed.
29 | EL-06: description shall be added here and in legend. |  |  | Updated in next revision. |  |  | Closed.
30 | EL.09: Specify the CT and Ammeter's data completely. |  |  | Updated in next revision. |  |  | Closed.
31 | EL.10: Use 3K12 to indicate Running and Stopped position of the motor. (use 2 signal lamps) |  |  | This can't be changed since this is per P&ID design |  |  | Closed.
32 | EL.12: Specify the type and rating of C.B. |  |  | Updated in next revision. |  |  | Closed.
33 | EL.15: It seems using this aux. relay as Heater Running in this part of the circuit is not sounds suitable, because after that there is a SSR switch and it might be in open status. Please check and clarify. |  |  | Updated and clarified. |  |  | Closed.
34 | EL.13: Please clarify about the thyristor switch. Add all switch data beside of it, |  |  | Not possible this shall be in the spare part list will be provided later. |  |  | Closed.
35 | EL.16: Does SSR have any error contact to using in circuit? |  |  | Updated |  |  | Closed.
36 | EL.14: Add all aux. relay's name beside them. |  |  | Description added |  |  | Closed.
37 | EL.18: Panel layout arrangement shall be prepared and issued. |  |  | Noted |  |  | Closed.
38 | EL.19: Part list shall be added in document. |  |  | Part list is another document the spare part list. |  |  | Closed.
38 | EL.20: Other parts of the wiring document shall be checked by Instrument dep. |  |  | Noted |  |  | Closed.
Revision 03
39 | Instead of PID controller please consider one analog output card in your PLC to control PV-10151, when you have PLC, using PID controller is not accepted. |  |  | Accoording to a teams meeting with Airpack at 14-06-2022, PID controller is approved.
40 | Fan shall be supplied from UPS power supply. |  |  | Noted, connected to the 24 Vdc circuit. So the fan is connect to both UPS's. Only not the 110 Vac but the 24Vdc.
41 | Changend LCP_COMB cable is 20Px1mm2, not the same as cable list. |  |  | Changend LCP_COMB cable from 20Px0.75m22 to 10Px0.75mm2, accoording to cable list (page 14)
42 | Signals tag number as per I/O list shall be specified. See page 16,39 |  |  | Noted, tagnumber added
43 | Signals tag number as per I/O list shall be specified. See page 17,40 |  |  | Noted, tagnumber added
44 | Signals tag number as per I/O list shall be specified.(HS-71121-SD) , see page 27,50,55 |  |  | Noted, tagnumber added
45 | Signals tag number as per I/O list shall be specified. (XS-71122-ST/SP) and (XS-71123-ST/SP), see page 30,53, |  |  | Noted, tagnumbers specified
46 | Please modify "common alarm" to "S/D Status" (see page 30,53,57) |  |  | Noted, tagname change from common Alarm to S/D Status
47 | Signal tag number Compressor B Remote HS-71105 is not correct, page 37 |  |  | Noted, changed tagnumber from HS-71105 to HS-17701
48 | Change TR_COMB cable to 10Px0,75mm2 , As per your cable list, vendor must considered 10Px0.75 mm2 cable, accordingly termination shall be modified, see page JIAX-C7080-01 - page 5 |  |  | noted but -> It is recommended to use +/- 20P x 0.75 cable due to a shortage of spare pairs. Cable is now changed form 20P to 10P
| Repeated Comment , 10Px0,75 mm², Rev03 page 102. Cable LCP_COMB. |  |  | It is recommended to use +/- 15P x 0.75 cable due to a shortage of Signals and spare pairs. Else there none spare 'pairs' available. Can also upgrade the cable to 20p x 0.75. Cable is now changed form 20P to 10P
| Signals tag no. shall be specified same as previous revision (terminal wiring diagrams) |  |  | Noted and specified
| Repeated comment, 5Px0.75mm2 Rev03 page 6 (LCP) |  |  | Noted and changed
| "Running" and "stopped" positions of motor shall be specified with signal lamps. Mentioned positions can be shown by status of this contactor. |  |  | noted, added two (2) signal lights, one led is een stopped indication and another one (1) is running light indication
| Moved '3H10' from X3 to X5 and used 2 pairs of the calbe FCNDX-C7080-LCP01 To connect the signal to the UCP. Because cable LCP_COMB run out of pairs (is only 10Px0.75mm2). |  |  | Noted