## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 27/Jul/2022 | Rev.:03
|  | Comment Sheet Ref.No.: | Doc Description: SINGLE LINE DIAGRAM FOR POWER DISTRIBUTION PANEL FOR NITGROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-00169 | Doc. No.: BU-20-VD-303-EL-DIG-0049
|  | Transmittal Date: 27/Jul/2022 | Doc Rev.: 03
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | EL.01: Add following data in the box. From: SWB3A-03(0.4KV) |  |  | Updated in next revision |  |  | Refer to document.
2 | EL.02: Required circuit breakers shall be considered and shown it in POWER DISTRIBUTION PANEL. (for Incoming and Outgoings ) |  |  | Mcb's are used for incoming power as project specification |  |  | It seems that using MCB for incoming is not suitable due to range of current. Additional information (sizing) shall be announced.
3 | Please clarify about connection between UCP and PDP with 20x1 mm2 cable. |  |  | This is the multicore cable for all the signals between the UCP and PDP check wiring diagram |  |  | According to cable schedule 10Px0.75mm2 has been considered
4 | EL03:this document should have SLD structure, but it is similar to a block diagram, not a single line diagram |  |  | This is the Airpack single line diagram as per project specification |  |  | Attached sample SLD shall be taken into consideration by airpack
5 | Redundant UPS power supply to UCP to be specified. |  |  | Redundant power supply in used for the UCP |  |  | Noted, but it must be specified in the document.
6 | EL: Why is this tag different in each document??!! In "Cable List" document: Oil Heater (LG-10151) Which one is finally true? |  |  | LG-10151 according to the wiring diagram. |  |  | Noted
7 | EL: Repeated Comment: Generally, this document is not a "Single Line Diagram". Considered protection for incoming and outgoings of "Power Distribution Panel" shall been shown in document. In addition, type of all CBs and related information such as rated current, breaking capacity and ... shall be added. |  |  | Noted. The layout and information of the document will be updated. |  |  | Type of all CBs and related information such as rated current, breaking capacity and ... shall be added.
8 | EL: Isn't it necessary to consider this cable in "Cable List"document? |  |  | Yes, It is. |  |  | Vendor confirmed that this cable shall be added in "Cable List" document. So, Noted.
9 | According to cable schedule 10Px0.75mm2 has been considered |  |  | Noted.
10 | EL: 3x150+70 mm2 | [5 empty] | Noted
11 | Repeated Comment - Redundant UPS power supply to UCP to be specified. |  |  | Noted.
12 | EL: "20-MS-SWB3B-01" |  |  | Noted. |  |  | Vendor has not been modified this tag.
13 | EL: "CU/XLPE/SWA/PVC" |  |  | Noted. |  |  | Noted
14 | Nitrogen Gas Booster 20-C-1002 |  |  | Noted. |  |  | Vendor has not been modified this tag.
15 | "20-MS-SWB3B-01" |  |  | Noted |  |  | Noted
15 | 20-C-1002-M |  |  | Noted |  |  | Noted
16 | All symbols shall be described in legend. Moreover, using MCB for incoming is not suitable due to range of current. |  |  | Added |  |  | Noted
17 | According to Cable List, it shall be 3x2.5 mm2. |  |  | Noted |  |  | Noted
18 | Suitable sizing of CBs for internal wiring is in vendor responsibility. |  |  | Updated |  |  | Vendor confirmed it. So, noted.
19 | Repeated Comment: Type of all CBs and related information such as rated current, breaking capacity and ... shall be added. |  |  | Updated |  |  | Noted
20 | Add rated power of this item. Add Cable Size of this item. |  |  | Added |  |  | Noted
21 | Add Cable Size of this item. |  |  | Added |  |  | Noted
15
22 | EL: What is difference between theses circuit breakers? |  |  | The first one is a moulded case circuit breaker (MCCB), the second one is a single pole miniature circuit breaker (MCB). Will be updated in the next revision.
23 | EL: Vendor shall clarify this item. Is it contactor? |  |  | Correct, will be updated in the next revision.
24 | EL: Are they the similar??? |  |  | No they are not, will be updated in the next revision.
25 | EL: Type of CB shall be clarified. For example: MCB, MCCB, ACB, … |  |  | Noted will be updated in the next revision
26 | EL: Type of CB shall be clarified. For example: MCB, MCCB, ACB, ... |  |  | Noted will be updated in the next revision
27 | EL: What is this number? Rated current is 100A or 160A? Type of CB shall be clarified. |  |  | Noted type will be clarified in legend. 100A will be updated in the next revision.
28 | EL: Cable Size = 4x25 mm2 |  |  | 4x25mm^2 will be updated in the next revision
29 | EL: What is this number? 0/115A??? 65/115A??? |  |  | Will be updated in the next revision
30 | EL: What is this number? Rated current is 100A or 160A? Type of CB shall be clarified. |  |  | 100A, will be updated in the next revision