## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 27/Jul/2022 | Rev.:04
|  | Comment Sheet Ref.No.: | Doc Description: SINGLE LINE DIAGRAM FOR POWER DISTRIBUTION PANEL FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00169 | Doc. No.: BU-20-VD-303-EL-DIG-0097
|  | Transmittal Date: 27/Jul/2022 | Doc Rev.: 04
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | EL.02: Required circuit breakers shall be considered and shown it in POWER DISTRIBUTION PANEL. (for Incoming and Outgoings ) |  |  | Updated in next revision CES REPLY: Please see comment inside document |  |  | It has not been added in the document yet.
2 | EL.01: Add following data in the box. From: SWB3A-03(0.4KV) Cable no: EBP-20-C-7080-M Cable Type and Size: CU/XLPE/AWA/PVC3.5*50mm2 Gland: EX-IP66, C2/M40 |  |  | Updated in next revision CES REPLY: Please see comment inside document |  |  | Noted
3 | Comments Rev.01 below
4 | EL.01: Add following data in the box. From: SWB3A-03(0.4KV) |  |  | Updated in next revision |  |  | Noted
5 | EL.02: Required circuit breakers shall be considered and shown it in POWER DISTRIBUTION PANEL. (for Incoming and Outgoings ) |  |  | Mcb's are used for incoming power as project specification |  |  | It seems that using MCB for incoming is not suitable. Additional information (sizing) shall be announced.
6 | Please clarify about connection between UCP and PDP with 20x1 mm2 cable. |  |  | This is the multicore cable for all the signals between the UCP and PDP check wiring diagram |  |  | According to cable schedule 10Px0.75mm2 has been considered
7 | EL03:this document should have SLD structure, but it is similar to a block diagram, not a single line diagram |  |  | This is the Airpack single line diagram as per project specification |  |  | Attached sample SLD shall be taken into consideration by airpack
8 | Redundant UPS power supply to UCP to be specified. |  |  | Redundant power supply in used for the UCP |  |  | Noted, but it must be specified in the document.
9 | EL: Repeated Comment: Generally, this document is not a "Single Line Diagram". Considered protection for incoming and outgoings of "Power Distribution Panel" shall been shown in document. In addition, type of all CBs and related information such as rated current, breaking capacity and ... shall be added. |  |  | Noted. The layout and information of the document will be updated.
10 | EL: Isn't it necessary to consider this cable in "Cable List"document? |  |  | Yes, It is.
11 | According to cable schedule 10Px0.75mm2 has been considered |  |  | Noted
12 | Repeated Comment - Redundant UPS power supply to UCP to be specified. |  |  | Noted
13 | EL: What is 7002? |  |  | Noted
14 | EL: "CU/XLPE/SWA/PVC" |  |  | Noted
15 | EL: 3x50+25 mm2 |  |  | Noted
16 | SWB3A-03 |  |  | Updated |  |  | Noted
17 | According to Cable List, it shall be M40. |  |  | Updated |  |  | Noted
18 | According to Cable List, it shall be 3.5x50 mm2. |  |  | Updated |  |  | Noted
19 | All symbols shall be described in legend. Moreover, using MCB for incoming is not suitable due to range of current. |  |  | Added |  |  | Noted
20 | Suitable sizing of CBs for internal wiring is in vendor responsibility. |  |  | Noted |  |  | Noted
21 | Repeated Comment: Type of all CBs and related information such as rated current, breaking capacity and ... shall be added. |  |  | Noted |  |  | Noted
22 | Add Cable Size of this item. |  |  | Added |  |  | Noted
23 | Add rated power of this item. Add Cable Size of this item. |  |  | Updated |  |  | Noted
15
22 | EL: What is difference between theses circuit breakers? |  |  | The first one is a moulded case circuit breaker (MCCB), the second one is a single pole miniature circuit breaker (MCB). Will be updated in the next revision.
23 | EL: Vendor shall clarify this item. Is it contactor? |  |  | Correct, will be updated in the next revision.
24 | EL: Are they the similar??? |  |  | No they are not, will be updated in the next revision.
25 | EL: Type of CB shall be clarified. For example: MCB, MCCB, ACB, … |  |  | Noted will be updated in the next revision
26 | EL: Type of CB shall be clarified. For example: MCB, MCCB, ACB, ... |  |  | Noted will be updated in the next revision
27 | EL: What is this number? Rated current is 28A or 40A? Type of CB shall be clarified. |  |  | Noted type will be clarified in legend. 28-40A will be updated in the next revision.
28 | EL: Cable Size shall be added. |  |  | Noted will be updated in the next revision
29 | EL: What is this number? 0/32A??? |  |  | 23-32 A, will be updated in the next revision
30 | EL: Additional information shall be added. For example rated current and ..... |  |  | Noted will be updated in the next revision