## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 17/Aug./2022 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: UTILITY CONSUMPTION LIST FOR NITROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-00176 | Doc. No.: BU 20 VD 303 PR LST 0014
|  | Transmittal Date: 17/Aug/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification
1 | 1. Please be noted that the purpose of the utility consumption document is reporting the utilities which consume in a unit. so, for example, instrument air consumption of valve must be reported. |  |  | Noted they have been added CES Reply (Jul.27,2022): Please refer to comments on the document.
2 | Air consumption for control valve, on-off valve and solenoid valve shall be specified. |  |  | Noted they have been added CES Reply (Jul.27,2022): Closed.
3 | .- Please specify workstations power consumption. - Number of required UPS and non-UPS feeders shall be specified as a note. - UPS and non-UPS power consumption shall be reviewed and consumption detail shall be submitted. |  |  | this has been deleted from this document, there is a separate document where this has been incorperated CES Reply (Jul.27,2022): Closed.
4 | EL: Vendor shall add additional information in accordance with attached file. A sample file has been attached into this file. Moreover, other electrical loads shall be added to the above table. |  |  | Noted they have been added CES Reply (Jul.27,2022): Closed. All electrical data shall be shown in separate document (electrical load list).
6 | 2. Considering this fact that the control valve and the solenoid valve consume instrument air the title must change to "Instrument Air". Please specify, is the instrument air at the battery limit of package required or not? |  |  | instrument air is not required, we will use internal supply of Nitrogen for these valves.
7 | Please insert a column and show the AIR or NITROGEN consumption. |  |  | Not required as we use Nitroge for the valves inside the package.
8 | 1. Please be noted that the nitrogen which is compressed by the compressor is not counted as utility. This row must be deleted. |  |  | Noted will be deleted
9 | With reference to vendor PID, AIRPACK stated that required nitrogen will be supplied from inside of package and there is no need to supply separate line for instrument air or nitrogen at the battery limit of package. Please confirm. |  |  | This is confirmed
10
11
12