## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 17/Aug./2022 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: UTILITY CONSUMPTION LIST FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00176 | Doc. No.: BU 20 VD 303 PR LST 0067
|  | Transmittal Date: 17/Aug/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification
1 | 1. Please be noted that the purpose of the utility consumption document is reporting the utilities which consume in a unit. so, for example, instrument air consumption of valve must be reported. |  |  | Noted they have been added CES Reply (Jul.27,2022): Please refer to comments on the document.
2 | Air consumption for control valve, on-off valve and solenoid valve shall be specified. |  |  | Noted they have been added CES Reply (Jul.27,2022): Closed.
3 | .- Please specify workstations power consumption. - Number of required UPS and non-UPS feeders shall be specified as a note. - UPS and non-UPS power consumption shall be reviewed and consumption detail shall be submitted. |  |  | this has been deleted from this document, there is a separate document where this has been incorperated CES Reply (Jul.27,2022): Closed.
4 | EL: Vendor shall add additional information in accordance with attached file. A sample file has been attached into this file. Moreover, other electrical loads shall be added to the above table. |  |  | Noted they have been added CES Reply (Jul.27,2022): Closed. All electrical data shall be shown in separate document (electrical load list).
5
6 | . Please be noted that the instrument air which is compressed by the compressor is not counted as utility. This row must be deleted. |  |  | Noted will be deleted
7 | Please insert a column and show the AIR or NITROGEN consumption. |  |  | No required this is only air
8 | With reference to vendor PID, AIRPACK stated that required air will be supplied from inside of package and there is no need to supply separate line for instrument air or nitrogen at the battery limit of package. Please confirm. |  |  | this is confirmed
9
10
11
12