## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 11/11/2022 | Rev.:08
|  | Comment Sheet Ref.No.: | Doc Description: SINGLE LINE DIAGRAM FOR POWER DISTRIBUTION PANEL FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00195 | Doc. No.: BU-20-VD-303-EL-DIG-0097
|  | Transmittal Date: 11/11/2022 | Doc Rev.: 08
(On Rev 6)1401/06/27
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply | CES Reply | CES Replay
1 | EL.02: Required circuit breakers shall be considered and shown it in POWER DISTRIBUTION PANEL. (for Incoming and Outgoings ) |  |  | Updated in next revision CES REPLY: Please see comment inside document |  |  | It has not been added in the document yet. | Noted | -
2 | EL.01: Add following data in the box. From: SWB3A-03(0.4KV) Cable no: EBP-20-C-7080-M Cable Type and Size: CU/XLPE/AWA/PVC3.5*50mm2 Gland: EX-IP66, C2/M40 |  |  | Updated in next revision CES REPLY: Please see comment inside document |  |  | Noted |  | -
3 | Comments Rev.01 below
4 | EL.01: Add following data in the box. From: SWB3A-03(0.4KV) |  |  | Updated in next revision |  |  | Noted |  | -
5 | EL.02: Required circuit breakers shall be considered and shown it in POWER DISTRIBUTION PANEL. (for Incoming and Outgoings ) |  |  | Mcb's are used for incoming power as project specification |  |  | It seems that using MCB for incoming is not suitable. Additional information (sizing) shall be announced. | MCCB has been added by vendor. So, Noted. | -
6 | Please clarify about connection between UCP and PDP with 20x1 mm2 cable. |  |  | This is the multicore cable for all the signals between the UCP and PDP check wiring diagram |  |  | According to cable schedule 10Px0.75mm2 has been considered |  | BY INSTRUMENT DEP
7 | EL03:this document should have SLD structure, but it is similar to a block diagram, not a single line diagram |  |  | This is the Airpack single line diagram as per project specification |  |  | Attached sample SLD shall be taken into consideration by airpack | Noted | -
8 | Redundant UPS power supply to UCP to be specified. |  |  | Redundant power supply in used for the UCP |  |  | Noted, but it must be specified in the document. |  | Noted, but it must be specified in the document.
9 | EL: Repeated Comment: Generally, this document is not a "Single Line Diagram". Considered protection for incoming and outgoings of "Power Distribution Panel" shall been shown in document. In addition, type of all CBs and related information such as rated current, breaking capacity and ... shall be added. |  |  | Noted. The layout and information of the document will be updated. |  |  | Noted |  | -
10 | EL: Isn't it necessary to consider this cable in "Cable List"document? |  |  | Yes, It is. |  |  | Noted |  | -
11 | According to cable schedule 10Px0.75mm2 has been considered |  |  | Noted |  |  |  |  | -
12 | Repeated Comment - Redundant UPS power supply to UCP to be specified. |  |  | Noted |  |  |  |  | -
13 | EL: What is 7002? |  |  | Noted |  |  | Noted |  | -
14 | EL: "CU/XLPE/SWA/PVC" |  |  | Noted |  |  | Noted |  | -
15 | EL: 3x50+25 mm2 |  |  | Noted |  |  | Noted |  | -
16 | SWB3A-03 |  |  | Updated |  |  | Noted |  | -
17 | According to Cable List, it shall be M40. |  |  | Updated |  |  | Noted |  | -
18 | According to Cable List, it shall be 3.5x50 mm2. |  |  | Updated |  |  | Noted |  | -
19 | All symbols shall be described in legend. Moreover, using MCB for incoming is not suitable due to range of current. |  |  | Added |  |  | Noted |  | -
20 | Suitable sizing of CBs for internal wiring is in vendor responsibility. |  |  | Noted |  |  | Noted |  | -
21 | Repeated Comment: Type of all CBs and related information such as rated current, breaking capacity and ... shall be added. |  |  | Noted |  |  | Noted |  | -
22 | Add Cable Size of this item. |  |  | Added |  |  | Noted |  | -
23 | Add rated power of this item. Add Cable Size of this item. |  |  | Updated |  |  | Noted |  | -
15
22 | EL: What is difference between theses circuit breakers? |  |  | The first one is a moulded case circuit breaker (MCCB), the second one is a single pole miniature circuit breaker (MCB). Will be updated in the next revision. |  |  | Noted |  | -
23 | EL: Vendor shall clarify this item. Is it contactor? |  |  | Correct, will be updated in the next revision. |  |  | Noted |  | -
24 | EL: Are they the similar??? |  |  | No they are not, will be updated in the next revision. |  |  | Noted |  | -
25 | EL: Type of CB shall be clarified. For example: MCB, MCCB, ACB, … |  |  | Noted will be updated in the next revision |  |  | Noted |  | -
26 | EL: Type of CB shall be clarified. For example: MCB, MCCB, ACB, ... |  |  | Noted will be updated in the next revision |  |  | Noted |  | -
27 | EL: What is this number? Rated current is 28A or 40A? Type of CB shall be clarified. |  |  | Noted type will be clarified in legend. 28-40A will be updated in the next revision. |  |  | Noted |  | -
28 | EL: Cable Size shall be added. |  |  | Noted will be updated in the next revision |  |  | Noted |  | -
29 | EL: What is this number? 0/32A??? |  |  | 23-32 A, will be updated in the next revision |  |  | Noted |  | -
30 | EL: Additional information shall be added. For example rated current and ..... |  |  | Noted will be updated in the next revision |  |  | Refer to document |  | Noted
31 | EL: According to comment/reply sheet, MCB shall be added. |  |  | Thermal overload is not applicable , will be deleten in next revision. |  |  |  |  | Noted
32 | EL: According to comment/reply sheet, MCB shall be added. |  |  | Noted will be updated in the next revision |  |  |  |  | Noted
33 | EL: MCB and MPCB have been used together! Why? MCB shall be suitable for motor starting. |  |  | 2 reason 1. MPCB is used for its thermal protection. 2. Reference to own note in 17811-05A UCPLCPJB ADJUSTMENT SCHEDULE FOR NITROGEN GAS BOOSTER Rev.04, page 103: "MCB is not acceptable. (Using an MCB for motor protection is not acceptable.) It must be an MCCB or MPCB" & " It looks like this is not an MCCB. It could be bimetal. Seller should clarify." |  |  |  |  | Noted
34 | Contactor |  |  | Noted will be updated in the next revision |  |  |  |  | Noted
35 | MCB |  |  | Noted will be updated in the next revision |  |  |  |  | Noted
36 | MPCB |  |  | Noted will be updated in the next revision |  |  |  |  | Noted
37 | EL: Repeated Comment: Additional information shall be added. For example rated current and ...... |  |  | Noted will be updated in the next revision |  |  |  |  | Noted
38 | EL: Repeated Comment: Why hasn't type of CB been added by vendor? |  |  | Noted will be updated in the next revision |  |  |  |  | Noted
39 | MCB |  |  | Noted will be updated in the next revision |  |  |  |  | Noted
COMMENTED ON REV06
40 | to be corrected. 2P shall be used. |  |  | Noted. Changed to 3P according to BU-20-VD-303-EL-DWG-0059 Rev 03 and the wiring Diagram, BU-20-VD-303-IN-DIG-0093
41 | EBP-20-C-7080-M |  |  | Noted. Updated according to wiring diagram
42 | 100 A OR 28-40? |  |  | Noted. 63A According to wiring Diagram
43 | TAG NO FOR DEVICES TO BE CHECKED ACCORDING TO BU-20-VD-303-EL-DWG-0059 |  |  | Noted. Updated according to BU-20-VD-303-EL-DWG-0059 Rev 03 and the wiring Diagram, BU-20-VD-303-IN-DIG-0093
COMMENTED ON REV07
44 | EL: After eight revision, vendor has been submitted wrong document!!! It is Emergency Instrument Air Compressor with tag number C-7080 |  |  | Updated.
45 | EL: It is Emergency Instrument Air Compressor with tag number C-7080 |  |  | Updated.