## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 28/Nov/2022 | Rev.: 06
|  | Comment Sheet Ref.No.: | Doc Description: UCP/LCP/JB GENERAL ARRANGEMENT DRAWING & TERMINAL DETAILS FOR EMERGENCY INSTRUMENT AIR COMPRESSOR INCL. BOM INCL. CRS
|  | Transmittal No.: APCES-V-00200 | Doc. No.: BU-20-VD-303-IN-DWG-0089
|  | Transmittal Date: 28/Nov/2022 | Doc Rev.: 06
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | 7M11 |  |  | Updated in next revision |  |  | Closed.
2 | Quint diode module to be specified. Terminals to be specified |  |  | Updated in next revision |  |  | Closed.
3 | Quantity and model number column to be added and specified too. |  |  | Quantity added, model number will be included in the spare part list this is another document |  |  | Closed.
4 | Panel lifting lugs and its details to be specified. |  |  | Updated in next revision |  |  | Closed.
5 | Ventilation system fitted with dust filters and with extraction fans mounted on the top of cabinets shall be provided. |  |  | Fan outlet filter at the top and the fan motor is at the bottem |  |  | Closed.
6 | To be separate to two earth bar ISE and NISE |  |  | ISE and Pe Bar check wiring diagram |  |  | Closed.
7 | For JB drawing requirement such as name plate, tag plate, terminal arrangement and etc. please refer to attached file |  |  | Noted |  |  | Required data as per attached file was not implemented.(such as name plate, special label and etc.)
1 | 16 terminal |  |  | Confirmed |  |  | Closed.
2 | Terminal drawing detail same as attached file to be specified |  |  | Rear side can not be shown this is not part of the panel layout Confirmed separation of 24VDC and 230VAC in all trunking and ways |  |  | Closed.
3 | Please modify to 5x 1x is sufficient |  |  | Updated in next revision |  |  | Closed.
4 | (RAL 9006) Gray Refer to clause M33 of TCL Eex'd' to be considered |  |  | This is (RAL 6021) Green Eex 'e' junction box as per project specification for terminal junction boxes |  |  | Closed.
5 | For JB drawing requirement such as name plate, tag plate, terminal arrangement and etc. please refer to attached file |  |  | Noted |  |  | Required data as per attached file was not implemented.(such as name plate, special label and etc.)
6 | 31 terminal |  |  | X2 has now 61 terminals |  |  | Closed.
7 | 1x is sufficient |  |  | Updated in next revision |  |  | Closed.
8 | EL-04: ammeter shall be considered. |  |  | Ammeter is mounted on the distribution panel check P&ID |  |  | Noted
9 | EL02: 1- The rear of the door shall be shown with mounted devices and wiring channel. 2-The suitable provision shall be considered for separation of 24Vdc and 230VAC in all trunking and ways. |  |  | Rear side can not be shown this is not part of the panel layout Confirmed separation of 24VDC and 230VAC in all trunking and ways |  |  | 1- Noted 2- Noted
10 | EL-03: The terminal Strip code is specified, but terminal numbers shall be add too. |  |  | Updated in next revision |  |  | Noted
11 | EL01: The technical specifications shall be completed in nameplate. The below items shall be added in name plate: -The degree of protection panel -The permissible withstanding short circuit current -The total weight of panel -The insulation voltage of panel -Manufacturer date -The panel tag |  |  | Confirmed |  |  | Vendor confirmed that but any actions have not been done on document.
12 | Modify the MC logo |  |  | Format is the same as the P&ID |  |  | Closed.
13 | BU-20-VD-303-IN-DWG-0039 01 |  |  | Updated in next revision |  |  | Closed.
14 | Repeated Comment: Ventilation system fitted with dust filters and with extraction fans mounted on the top of cabinets shall be provided. (Fans motor shall be on the top of the panel and filter must be at the bottom of front door.) |  |  | Updated in next revision
15 |  |  |  | Closed.O15:I3026
17
18
19
20 |  |  |  | Closed.O15:I3026
Rev 03
21 | PE is protective earth for panel earthing, for IS and NIS signals separate earth bar shall be considered. |  |  | Updated in next revision
22 | As per instrument cable list M25 cable gland shall be considered |  |  | Updated in next revision
23 | Required data as per attached file (in previous rev.) was not implemented.(such as name plate, special label and etc.) |  |  | Updated in next revision
24 | According to selecting Eex'd' type solenoid valve, so selected JB shall be Eex'd' too. JB protection shall be considered Eex'd' and its color shall be RAL9006 |  |  | Updated in next revision
25 | According to selecting Eex'd' type solenoid valve, so selected JB shall be Eex'd' too. JB protection shall be considered Eex'd' and its color shall be RAL9006 |  |  | As agreed the junction box remains ex'e , the color of the junction box will be updated in the next revision
26 | Required data as per attached file (in previous rev.) was not implemented.(such as name plate, special label and etc.) |  |  | Already included
27 | This is tag plate that you specified, in addition tag plate, name plate and special label (same as attached file in previous rev.) shall be specified in this document. |  |  | Updated in next revision
28 | Regarding to considering one JB for analogue input/outputs so one terminal strip and one multi cable 10Px0,75 mm² will be considered for this JB, accordingly X2 and X3 shall be merged in to one terminal strip. |  |  | Updated in next revision
29 | To be deleted |  |  | Updated in next revision
30 | This is tag plate that you specified, in addition tag plate, name plate and special label (same as attached file in previous rev.) shall be specified in this document. |  |  | Updated in next revision
31 | LCP shall be Eex'd' type JB, regarding to NIS signals contain it. accordingly its color shall be RAL9006 |  |  | As agreed the junction box remains ex'e , the color of the junction box will be updated in the next revision
32 | This is tag plate that you specified, in addition tag plate, name plate and special label (same as attached file in previous rev.) shall be specified in this document. |  |  | Updated in next revision
33 | M25 |  |  | Updated in next revision
34 | EL: Repeated Comment: The technical specifications shall be completed in nameplate. The below items shall be added in name plate: -The degree of protection panel -The permissible withstanding short circuit current -The total weight of panel -The insulation voltage of panel -Manufacturer date -The panel tag |  |  | The data that will be fixed at a later stage, there is a note made on the drawing with the data that will be incorporated into the nameplate as soon as it is known. (note6)dated in next revision |  |  | Noted
Rev04
35 | All components model no. shall be added. |  |  | Updated in next revision. The model numbers are not official yet, it depends on what the market does. It is possible that it will still change over time. |  |  | Closed. See document.
36 | Modify the MC logo |  |  | Noted, will be updated in the next revision. |  |  | Closed. See document.
37 | 2 |  |  | Noted, will be updated in the next revision. |  |  | Closed. See document.
38 | 2 |  |  | Noted, will be updated in the next revision. |  |  | Closed. See document.
39 | Repeated Comment Required data as per attached file (in previous rev.) was not implemented.(such as name plate, special label and etc.) |  |  | Noted, will be updated in the next revision. |  |  | Closed. See document.
40 | According to your TQ, we accepted that you using Eex 'e' JB, so color of Eex 'e' JB shall be RAL 6021. |  |  | Noted, will be updated in the next revision. |  |  | Closed. See document.
41 | Repeated Comment This is tag plate that you specified, in addition tag plate, name plate and special label (same as attached file in previous rev.) shall be specified in this document. |  |  | Noted, will be updated in the next revision. |  |  | Closed. See document.
42 | Repeated Comment This is tag plate that you specified, in addition tag plate, name plate and special label (same as attached file in previous rev.) shall be specified in this document. |  |  | Noted, will be updated in the next revision. |  |  | Closed. See document.
43 | According to your TQ, we accepted that you using Eex 'e' JB, so color of Eex 'e' JB shall be RAL 6021. |  |  | Noted, will be updated in the next revision. |  |  | Closed. See document.
44 | Repeated Comment This is tag plate that you specified, in addition tag plate, name plate and special label (same as attached file in previous rev.) shall be specified in this document. |  |  | Noted, will be updated in the next revision. |  |  | Closed. See document.
Rev05
45 | 3 |  |  | Updated. |  |  | Closed
46 | 3 |  |  | Updated. |  |  | Closed
47 | EL: This document shall match "UCP/LCP/JB WIRING DIAGRAM FOR EMERGENCY INSTRUMENT AIR COMPRESSOR" document. All changes in "wiring diagram" document shall be added here. Such as Signal Lamp, Push Button and ..... Moreover, Tag number for equipment shall match "wiring diagram" document. |  |  | Updated to Wiring Diagram Rev 7 |  |  | Closed
48 | EL: Texts are not readable. The quality is very low. |  |  | Printing properties updated. |  |  | Closed
49 | This note is not accepted and must be deleted. document must be revised based on final data. |  |  | Updated. |  |  | Closed
50 | EL: Name and Document Number shall be added. |  |  | Updated. |  |  | Closed
51 | 3 |  |  | Updated. |  |  | Closed
52 | 3 |  |  | Updated. |  |  | Closed
53 | Gland entry details must be specified |  |  | Updated. |  |  | Closed
54 | Another label same as this label with following content must be added : "Explosion Hazard, Disconnect Signals before Maintenance" |  |  | Updated. |  |  | Closed
55 | White letter on Red background |  |  | Updated. |  |  | Closed
56 | JNDX-C7080-01 |  |  | Updated. |  |  | Closed
57 | THIS BOX CONTAINS NON-INTRINSICALLY SAFE SIGNALS |  |  | Updated. |  |  | Closed
58 | 3 |  |  | Updated. |  |  | Closed
59 | 3 |  |  | Updated. |  |  | Closed
60 | 10X |  |  | Updated. |  |  | Closed
61 | Repeated Comment This is tag plate that you specified, in addition tag plate, name plate and special label (same as attached file in previous rev.) shall be specified in this document. |  |  | Updated. |  |  | Closed
62 | 3 |  |  | Updated. |  |  | Closed
63 | 3 |  |  | Updated. |  |  | Closed
64 | 3 |  |  | Updated. |  |  | Closed
65 | 3 |  |  | Updated. |  |  | Closed
66 | Items code number must be modified according to previous page table. |  |  | Updated. |  |  | Closed
67 | EL: This document shall match "UCP/LCP/JB WIRING DIAGRAM FOR EMERGENCY INSTRUMENT AIR COMPRESSOR" document. All changes in "wiring diagram" document shall be added here. Such as Signal Lamp, Push Button and ..... Moreover, Tag number for equipment shall match "wiring diagram" document. |  |  | Updated to Wiring Diagram Rev 7 |  |  | Closed
68 | Location of name plate and label on the JB door must be specified. |  |  | Updated. |  |  | Closed
69 | Another label same as this label with following content must be added : "Explosion Hazard, Disconnect Signals before Maintenance" |  |  | Updated. |  |  | Closed
70 | EL: Name and Document Number shall be added. |  |  | Updated. |  |  | Closed
71 | 3 |  |  | Updated. |  |  | Closed
72 | White letter on Red background |  |  | Updated. |  |  | Closed
73 | Green |  |  | Updated. |  |  | Closed
74 | 3 |  |  | Updated. |  |  | Closed
Rev06
75 | Please clarify why ESD relay has been removed. |  |  | ESD Relay added back to Panel Layout Drawing as per Wiring Diagram.
76 | Shall be in one cell |  |  | Updated.
77 | Please clarify why ESD relay has been removed. |  |  | ESD Relay added back to Panel Layout Drawing as per Wiring Diagram.
78 | Communication module shall be specified. |  |  | Updated.
79 | specified codes have been discrepancy with BOM table (previous page table) |  |  | Updated.
80 | Label content shall be modified |  |  | Updated on all pages.
81 | EL: Conflict with wiring document. Vendor shall check it again. |  |  | Updated.
Rev07
82 | Repeated Comment Label content shall be modified (THIS BOX CONTAINS NON-INTRINSICALLY SAFE SIGNALS) |  |  | Updated.
83 | THIS BOX CONTAINS NON-INTRINSICALLY SAFE SIGNALS |  |  | Updated.