## Resolution Sheet
PROJECT:
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Instrument datasheet | 23249-12
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | Page 1 | 00 |  | Instrument tag numbers to be corrected | Updated
2 | Page 1 | 00 |  | SIL level for each device shall be finalysed based on SIL study report | We have not received a SIL study report, please advise
3 | Page 1 | 00 |  | Hazardous area shall be considered ZONE2 IICT3 , please confirm | For instrumentation Zone 1 is considered.
4 | Page 4 | 00 |  | For pressure gauges , minimum , normal and maximum operating pressures to be specified | The available operating pressures are added.
5 | Page 7 | 00 |  | Min/norm/maximum flow range to be specified | Only operating flow is available
6 | Page 7 | 00 |  | type of flowgauge to be specified | Type is variable area
7 | Page 9 | 00 |  | 316 ss , insturmnt valve manifold for all pressure gauge & transmitter shall be supplied | Valve manifolds are not supplied as per project order |  |  |  | Open
8 | Page 13 | 00 |  | All data to be filled and specified | Added |  |  |  | Closed
9
10
11
12
13
14
15
16
17
18
19
20